## General
Excel file version | v2.0
Name | Distribution
Frequency (Hz) | 60
Power Base (MVA) | 100

## Pins
//outgoing | V_abs | 828_a/Vmag | 828_b/Vmag | 828_c/Vmag | 830_a/Vmag | 830_b/Vmag | 830_c/Vmag | 834_a/Vmag | 834_b/Vmag | 834_c/Vmag | 836_a/Vmag | 836_b/Vmag | 836_c/Vmag | 840_a/Vmag | 840_b/Vmag | 840_c/Vmag | 842_a/Vmag | 842_b/Vmag | 842_c/Vmag | 844_a/Vmag | 844_b/Vmag | 844_c/Vmag | 846_a/Vmag | 846_b/Vmag | 846_c/Vmag | 848_a/Vmag | 848_b/Vmag | 848_c/Vmag | 854_a/Vmag | 854_b/Vmag | 854_c/Vmag | 860_a/Vmag | 860_b/Vmag | 860_c/Vmag | 888_a/Vmag | 888_b/Vmag | 888_c/Vmag | 890_a/Vmag | 890_b/Vmag | 890_c/Vmag
//outgoing | V_ang | 828_a/Vang | 828_b/Vang | 828_c/Vang | 830_a/Vang | 830_b/Vang | 830_c/Vang | 834_a/Vang | 834_b/Vang | 834_c/Vang | 836_a/Vang | 836_b/Vang | 836_c/Vang | 840_a/Vang | 840_b/Vang | 840_c/Vang | 842_a/Vang | 842_b/Vang | 842_c/Vang | 844_a/Vang | 844_b/Vang | 844_c/Vang | 846_a/Vang | 846_b/Vang | 846_c/Vang | 848_a/Vang | 848_b/Vang | 848_c/Vang | 854_a/Vang | 854_b/Vang | 854_c/Vang | 860_a/Vang | 860_b/Vang | 860_c/Vang | 888_a/Vang | 888_b/Vang | 888_c/Vang | 890_a/Vang | 890_b/Vang | 890_c/Vang
//outgoing | I_abs | LN_828_830/ImagFrom1 | LN_828_830/ImagFrom2 | LN_828_830/ImagFrom3 | LN_830_854/ImagFrom1 | LN_830_854/ImagFrom2 | LN_830_854/ImagFrom3 | LN_834_842/ImagFrom1 | LN_834_842/ImagFrom2 | LN_834_842/ImagFrom3 | LN_834_860/ImagFrom1 | LN_834_860/ImagFrom2 | LN_834_860/ImagFrom3 | LN_836_840/ImagFrom1 | LN_836_840/ImagFrom2 | LN_836_840/ImagFrom3 | LN_836_862/ImagFrom1 | LN_836_862/ImagFrom2 | LN_836_862/ImagFrom3 | LN_842_844/ImagFrom1 | LN_842_844/ImagFrom2 | LN_842_844/ImagFrom3 | LN_844_846/ImagFrom1 | LN_844_846/ImagFrom2 | LN_844_846/ImagFrom3 | LN_846_848/ImagFrom1 | LN_846_848/ImagFrom2 | LN_846_848/ImagFrom3 | LN_854_852/ImagFrom1 | LN_854_852/ImagFrom2 | LN_854_852/ImagFrom3 | LN_854_856/ImagFrom1 | LN_860_836/ImagFrom1 | LN_860_836/ImagFrom2 | LN_860_836/ImagFrom3 | LN_888_890/ImagFrom1 | LN_888_890/ImagFrom2 | LN_888_890/ImagFrom3
//outgoing | I_ang | LN_828_830/IangFrom1 | LN_828_830/IangFrom2 | LN_828_830/IangFrom3 | LN_830_854/IangFrom1 | LN_830_854/IangFrom2 | LN_830_854/IangFrom3 | LN_834_842/IangFrom1 | LN_834_842/IangFrom2 | LN_834_842/IangFrom3 | LN_834_860/IangFrom1 | LN_834_860/IangFrom2 | LN_834_860/IangFrom3 | LN_836_840/IangFrom1 | LN_836_840/IangFrom2 | LN_836_840/IangFrom3 | LN_836_862/IangFrom1 | LN_836_862/IangFrom2 | LN_836_862/IangFrom3 | LN_842_844/IangFrom1 | LN_842_844/IangFrom2 | LN_842_844/IangFrom3 | LN_844_846/IangFrom1 | LN_844_846/IangFrom2 | LN_844_846/IangFrom3 | LN_846_848/IangFrom1 | LN_846_848/IangFrom2 | LN_846_848/IangFrom3 | LN_854_852/IangFrom1 | LN_854_852/IangFrom2 | LN_854_852/IangFrom3 | LN_854_856/IangFrom1 | LN_860_836/IangFrom1 | LN_860_836/IangFrom2 | LN_860_836/IangFrom3 | LN_888_890/IangFrom1 | LN_888_890/IangFrom2 | LN_888_890/IangFrom3
//outgoing | PQ_ld | LD_830/P1 | LD_830/Q1 | LD_830/P2 | LD_830/Q2 | LD_830/P3 | LD_830/Q3 | LD_840/P1 | LD_840/Q1 | LD_844/P1 | LD_844/Q1 | LD_844/P2 | LD_844/Q2 | LD_844/P3 | LD_844/Q3 | LD_848/P1 | LD_848/Q1 | LD_848/P2 | LD_848/Q2 | LD_848/P3 | LD_848/Q3 | LD_860/P1 | LD_860/Q1 | LD_890/P1 | LD_890/Q1 | LD_890/P2 | LD_890/Q2 | LD_890/P3 | LD_890/Q3
//incoming | Trans_tap | TR1_832_888/tap_1 | TR1_832_888/tap_2 | TR1_832_888/tap_3
//incoming | PQ_ld | LD_830/P1 | LD_830/Q1 | LD_830/P2 | LD_830/Q2 | LD_830/P3 | LD_830/Q3 | LD_840/P1 | LD_840/Q1 | LD_844/P1 | LD_844/Q1 | LD_844/P2 | LD_844/Q2 | LD_844/P3 | LD_844/Q3 | LD_848/P1 | LD_848/Q1 | LD_848/P2 | LD_848/Q2 | LD_848/P3 | LD_848/Q3 | LD_860/P1 | LD_860/Q1 | LD_890/P1 | LD_890/Q1 | LD_890/P2 | LD_890/Q2 | LD_890/P3 | LD_890/Q3

## Bus
Bus | Base Voltage (V) | Initial Vmag | Unit | Angle | Type
800_a | 15094.823 | 15094.823 | V | 0 | SLACK
800_b | 15094.823 | 15094.823 | V | -120 | SLACK
800_c | 15094.823 | 15094.823 | V | 120 | SLACK
802_a | 15094.823 | 15094.823 | V | 0 | PQ
802_b | 15094.823 | 15094.823 | V | -120 | PQ
802_c | 15094.823 | 15094.823 | V | 120 | PQ
806_a | 15094.823 | 15094.823 | V | 0 | PQ
806_b | 15094.823 | 15094.823 | V | -120 | PQ
806_c | 15094.823 | 15094.823 | V | 120 | PQ
808_a | 15094.823 | 15094.823 | V | 0 | PQ
808_b | 15094.823 | 15094.823 | V | -120 | PQ
808_c | 15094.823 | 15094.823 | V | 120 | PQ
810_b | 15094.823 | 15094.823 | V | -120 | PQ
812_a | 15094.823 | 15094.823 | V | 0 | PQ
812_b | 15094.823 | 15094.823 | V | -120 | PQ
812_c | 15094.823 | 15094.823 | V | 120 | PQ
814_a | 15094.823 | 15094.823 | V | 0 | PQ
814_b | 15094.823 | 15094.823 | V | -120 | PQ
814_c | 15094.823 | 15094.823 | V | 120 | PQ
816_a | 15094.823 | 15094.823 | V | 0 | PQ
816_b | 15094.823 | 15094.823 | V | -120 | PQ
816_c | 15094.823 | 15094.823 | V | 120 | PQ
818_a | 15094.823 | 15094.823 | V | 0 | PQ
820_a | 15094.823 | 15094.823 | V | 0 | PQ
822_a | 15094.823 | 15094.823 | V | 0 | PQ
824_a | 15094.823 | 15094.823 | V | 0 | PQ
824_b | 15094.823 | 15094.823 | V | -120 | PQ
824_c | 15094.823 | 15094.823 | V | 120 | PQ
826_b | 15094.823 | 15094.823 | V | -120 | PQ
828_a | 15094.823 | 15094.823 | V | 0 | PQ
828_b | 15094.823 | 15094.823 | V | -120 | PQ
828_c | 15094.823 | 15094.823 | V | 120 | PQ
830_a | 15094.823 | 15094.823 | V | 0 | PQ
830_b | 15094.823 | 15094.823 | V | -120 | PQ
830_c | 15094.823 | 15094.823 | V | 120 | PQ
832_a | 15094.823 | 15094.823 | V | 0 | PQ
832_b | 15094.823 | 15094.823 | V | -120 | PQ
832_c | 15094.823 | 15094.823 | V | 120 | PQ
834_a | 15094.823 | 15094.823 | V | 0 | PQ
834_b | 15094.823 | 15094.823 | V | -120 | PQ
834_c | 15094.823 | 15094.823 | V | 120 | PQ
836_a | 15094.823 | 15094.823 | V | 0 | PQ
836_b | 15094.823 | 15094.823 | V | -120 | PQ
836_c | 15094.823 | 15094.823 | V | 120 | PQ
838_b | 15094.823 | 15094.823 | V | -120 | PQ
840_a | 15094.823 | 15094.823 | V | 0 | PQ
840_b | 15094.823 | 15094.823 | V | -120 | PQ
840_c | 15094.823 | 15094.823 | V | 120 | PQ
842_a | 15094.823 | 15094.823 | V | 0 | PQ
842_b | 15094.823 | 15094.823 | V | -120 | PQ
842_c | 15094.823 | 15094.823 | V | 120 | PQ
844_a | 15094.823 | 15094.823 | V | 0 | PQ
844_b | 15094.823 | 15094.823 | V | -120 | PQ
844_c | 15094.823 | 15094.823 | V | 120 | PQ
846_a | 15094.823 | 15094.823 | V | 0 | PQ
846_b | 15094.823 | 15094.823 | V | -120 | PQ
846_c | 15094.823 | 15094.823 | V | 120 | PQ
848_a | 15094.823 | 15094.823 | V | 0 | PQ
848_b | 15094.823 | 15094.823 | V | -120 | PQ
848_c | 15094.823 | 15094.823 | V | 120 | PQ
850_a | 15094.823 | 15094.823 | V | 0 | PQ
850_b | 15094.823 | 15094.823 | V | -120 | PQ
850_c | 15094.823 | 15094.823 | V | 120 | PQ
852_a | 15094.823 | 15094.823 | V | 0 | PQ
852_b | 15094.823 | 15094.823 | V | -120 | PQ
852_c | 15094.823 | 15094.823 | V | 120 | PQ
854_a | 15094.823 | 15094.823 | V | 0 | PQ
854_b | 15094.823 | 15094.823 | V | -120 | PQ
854_c | 15094.823 | 15094.823 | V | 120 | PQ
856_b | 15094.823 | 15094.823 | V | -120 | PQ
858_a | 15094.823 | 15094.823 | V | 0 | PQ
858_b | 15094.823 | 15094.823 | V | -120 | PQ
858_c | 15094.823 | 15094.823 | V | 120 | PQ
860_a | 15094.823 | 15094.823 | V | 0 | PQ
860_b | 15094.823 | 15094.823 | V | -120 | PQ
860_c | 15094.823 | 15094.823 | V | 120 | PQ
862_a | 15094.823 | 15094.823 | V | 0 | PQ
862_b | 15094.823 | 15094.823 | V | -120 | PQ
862_c | 15094.823 | 15094.823 | V | 120 | PQ
864_a | 15094.823 | 15094.823 | V | 0 | PQ
888_a | 15094.823 | 15094.823 | V | 0 | PQ
888_b | 15094.823 | 15094.823 | V | -120 | PQ
888_c | 15094.823 | 15094.823 | V | 120 | PQ
890_a | 15094.823 | 15094.823 | V | 0 | PQ
890_b | 15094.823 | 15094.823 | V | -120 | PQ
890_c | 15094.823 | 15094.823 | V | 120 | PQ

## Voltage Source
Type
PositiveSeqVsource
SinglePhaseVsource
ThreePhaseShortCircuitVsource
ThreePhaseSequentialVsource
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Voltage Source |  |  |  | Go to Type List
ID | Bus | Voltage (pu) | Angle (deg) | Rs (pu) | Xs (pu)
End of Positive-Sequence Voltage Source
Single-Phase Voltage Source |  |  |  | Go to Type List
ID | Bus1 | Voltage (V) | Angle (deg) | Rs (Ohm) | Xs (Ohm)
End of Single-Phase Voltage Source
Three-Phase Voltage Source with Short-Circuit Level Data |  |  |  | Go to Type List
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | SC1ph (MVA) | SC3ph (MVA)
End of Three-Phase Voltage Source with Short-Circuit Level Data
Three-Phase Voltage Source with Sequential Data |  |  |  | Go to Type List
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | R1 (Ohm) | X1 (Ohm) | R0 (Ohm) | X0 (Ohm)
SRC_MAIN | 800_a | 800_b | 800_c | 24.9 | 0 | 0 | 0 | 0 | 0
End of Three-Phase Voltage Source with Sequential Data

## Load
Type
PositiveSeqZload | ThreePhaseZIPLoad
PositiveSeqPload
PositiveSeqIload
SinglePhaseZIPLoad
TwoPhaseZIPLoad
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Constant Impedance Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Constant Impedance Load
Positive-Sequence Constant Power Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Constant Power Load
Positive-Sequence Constant Current Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Constant Current Load
Single-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | P1 (kW) | Q1 (kVAr)
LD_808_810 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 808_b | 16 | 8
LD_828_830 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 828_a | 7 | 3
LD_842_844 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 842_a | 9 | 5
LD_820_822 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 820_a | 135 | 70
LD_862_838 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 862_b | 28 | 14
LD_818_820 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 818_a | 34 | 17
LD_824_828 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 824_c | 4 | 2
LD_824_826 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 824_b | 40 | 20
LD_858_864 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 858_a | 2 | 1
LD_816_824 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 816_b | 5 | 2
LD_854_856 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 854_b | 4 | 2
LD_846_848 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 846_b | 23 | 11
End of Single-Phase ZIP Load
Two-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | P1(kW) | Q1(kVAr) | P2 (kW) | Q2 (kVAr)
LD_802_806 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 802_b | 802_c | 30 | 15 | 25 | 14
LD_844_846 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 844_b | 844_c | 25 | 12 | 20 | 11
LD_836_840 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 836_a | 836_b | 18 | 9 | 22 | 11
End of Two-Phase ZIP Load
Three-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | Bus3 | P1(kW) | Q1(kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
LD_3 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 844_a | 844_b | 844_c | 135 | 105 | 135 | 105 | 135 | 105
LD_4 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 848_a | 848_b | 848_c | 20 | 16 | 20 | 16 | 20 | 16
LD_860_836 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 860_a | 860_b | 860_c | 30 | 15 | 10 | 6 | 42 | 22
LD_834_860 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 834_a | 834_b | 834_c | 16 | 8 | 20 | 10 | 110 | 55
LD_6 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 830_a | 830_b | 830_c | 10 | 5 | 10 | 5 | 25 | 10
LD_222_1 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 840_a | 840_b | 840_c | 9 | 7 | 9 | 7 | 9 | 7
LD_832_858 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 832_a | 832_b | 832_c | 7 | 3 | 2 | 1 | 6 | 3
LD_5 | 1 | 4.16 | 0.2 | wye | 0 | 0 | 1 | 0 | 890_a | 890_b | 890_c | 150 | 75 | 150 | 75 | 150 | 75
LD_222 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 860_a | 860_b | 860_c | 20 | 16 | 20 | 16 | 20 | 16
LD_858_834 | 1 | 24.9 | 0.2 | wye | 0 | 0 | 1 | 0 | 858_a | 858_b | 858_c | 4 | 2 | 15 | 8 | 13 | 7
End of Three-Phase ZIP Load

## Line
Type
PositiveSeqLine
SinglePhaseLine
TwoPhaseLine
ThreePhaseLineFullData
ThreePhaseLineSequentialData
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Line |  | Go to Type List
ID | Status | From bus | To bus | R (pu) | X (pu) | B (pu)
End of Positive-Sequence Line
Single-Phase Line |  | Go to Type List
ID | Status | Length | From1 | To1 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | b11 (uS/length_unit)
LN_808_810 | 1 | 1.0992 | 808_b | 810_b | 1.0809 | 0.57355 | 1.6313
LN_820_822 | 1 | 2.6023 | 820_a | 822_a | 1.0809 | 0.57355 | 1.6313
LN_862_838 | 1 | 0.92045 | 862_b | 838_b | 0.74197 | 0.54873 | 1.6848
LN_818_820 | 1 | 9.1193 | 818_a | 820_a | 1.0809 | 0.57355 | 1.6313
LN_824_826 | 1 | 0.57386 | 824_b | 826_b | 1.0809 | 0.57355 | 1.6313
LN_858_864 | 1 | 0.30682 | 858_a | 864_a | 0 | 0 | 0
LN_854_856 | 1 | 4.4186 | 854_b | 856_b | 1.0809 | 0.57355 | 1.6313
LN_816_818 | 1 | 0.32386 | 816_a | 818_a | 1.0809 | 0.57355 | 1.6313
End of Single-Phase Line
Two-Phase Line |  | Go to Type List
ID | Status | Length | From1 | From2 | To1 | To2 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit)
End of Two-Phase Line
Three-Phase Line with Full Data |  | Go to Type List
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | r31 (Ohm/length_unit) | x31 (Ohm/length_unit) | r32 (Ohm/length_unit) | x32 (Ohm/length_unit) | r33 (Ohm/length_unit) | x33 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit) | b31 (uS/length_unit) | b32 (uS/length_unit) | b33 (uS/length_unit)
LN_806_808 | 1 | 6.1042 | 806_a | 806_b | 806_c | 808_a | 808_b | 808_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_832_15 | 1 | 0.0018939 | 832_a | 832_b | 832_c | 15_a | 15_b | 15_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_854_852 | 1 | 6.9754 | 854_a | 854_b | 854_c | 852_a | 852_b | 852_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_808_812 | 1 | 7.1023 | 808_a | 808_b | 808_c | 812_a | 812_b | 812_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_800_802 | 1 | 0.48864 | 800_a | 800_b | 800_c | 802_a | 802_b | 802_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_828_830 | 1 | 3.8712 | 828_a | 828_b | 828_c | 830_a | 830_b | 830_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_860_836 | 1 | 0.50758 | 860_a | 860_b | 860_c | 836_a | 836_b | 836_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_842_844 | 1 | 0.25568 | 842_a | 842_b | 842_c | 844_a | 844_b | 844_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_834_860 | 1 | 0.38258 | 834_a | 834_b | 834_c | 860_a | 860_b | 860_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_802_806 | 1 | 0.32765 | 802_a | 802_b | 802_c | 806_a | 806_b | 806_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_850_816 | 1 | 0.058712 | 850_a | 850_b | 850_c | 816_a | 816_b | 816_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_844_846 | 1 | 0.68939 | 844_a | 844_b | 844_c | 846_a | 846_b | 846_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_824_828 | 1 | 0.15909 | 824_a | 824_b | 824_c | 828_a | 828_b | 828_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_836_862 | 1 | 0.05303 | 836_a | 836_b | 836_c | 862_a | 862_b | 862_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_832_858 | 1 | 0.92803 | 832_a | 832_b | 832_c | 858_a | 858_b | 858_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_812_814 | 1 | 5.6307 | 812_a | 812_b | 812_c | 814_a | 814_b | 814_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_834_842 | 1 | 0.05303 | 834_a | 834_b | 834_c | 842_a | 842_b | 842_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_816_824 | 1 | 1.9337 | 816_a | 816_b | 816_c | 824_a | 824_b | 824_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_836_840 | 1 | 0.16288 | 836_a | 836_b | 836_c | 840_a | 840_b | 840_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_846_848 | 1 | 0.10038 | 846_a | 846_b | 846_c | 848_a | 848_b | 848_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_814_850 | 1 | 0.0018939 | 814_a | 814_b | 814_c | 850_a | 850_b | 850_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_888_890 | 1 | 2 | 888_a | 888_b | 888_c | 890_a | 890_b | 890_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_830_854 | 1 | 0.098485 | 830_a | 830_b | 830_c | 854_a | 854_b | 854_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
LN_858_834 | 1 | 1.1042 | 858_a | 858_b | 858_c | 834_a | 834_b | 834_c | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 0.12427 | 0.43496 | 0.12427 | 0.43496 | 0.24855 | 0.86992 | 3.1069 | 0 | 3.1069 | 0 | 0 | 3.1069
End of Three-Phase Line with Full Data
Three-Phase Line with Sequential Data |  | Go to Type List
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | R0 (Ohm/length_unit) | X0 (Ohm/length_unit) | R1 (Ohm/length_unit) | X1 (Ohm/length_unit) | B0 (uS/length_unit) | B1 (uS/length_unit)
End of Three-Phase Line with Sequential Data

## Transformer
Type
PositiveSeq2wXF
PositiveSeq3wXF
Multiphase2wXF
Multiphase2wXFMutual
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence 2W-Transformer |  |  | Go to Type List
ID | Status | From bus | To bus | R (pu) | Xl (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Phase Shift (deg)
End of Positive-Sequence 2W-Transformer
Positive-Sequence 3W-Transformer |  |  | Go to Type List
ID | Status | Bus1 | Bus2 | Bus3 | R_12 (pu) | Xl_12 (pu) | R_23 (pu) | Xl_23 (pu) | R_31 (pu) | Xl_31 (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Ratio W3 (pu) | Phase Shift W1 (deg) | Phase Shift W2 (deg) | Phase Shift W3 (deg)
End of Positive-Sequence 3W-Transformer
Multiphase 2W-Transformer |  |  | Go to Type List
ID | Status | Number of phases | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | X (pu) | RW1 (pu) | RW2 (pu)
TR1_832_888 | 1 | 3 | 832_a | 832_b | 832_c | 24.9 | 500.001 | wye | 888_a | 888_b | 888_c | 4.16 | 500.001 | wye | 1 | 1 | 1 |  |  |  |  | 0.0408 | 0.0094999 | 0.0094999
End of Multiphase 2W-Transformer
Multiphase 2W-Transformer with Mutual Impedance |  |  | Go to Type List
ID | Status | Number of phases | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | Z0 leakage (pu) | Z1 leakage (pu) | X0/R0 | X1/R1 | No Load Loss (kW)
End of Multiphase 2W-Transformer with Mutual Impedance

## Switch
From Bus | To Bus | ID | Status

## Shunt
Type
PositiveSeqShunt
SinglePhaseShunt
TwoPhaseShunt
ThreePhaseShunt
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Shunt |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Shunt
Single-Phase Shunt |  | Go to Type List
ID | Status | kV (ph-gr RMS) | Bus1 | P1 (kW) | Q1 (kVAr)
End of Single-Phase Shunt
Two-Phase Shunt |  | Go to Type List
ID | Status1 | Status2 | kV (ph-gr RMS) | Bus1 | Bus2 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr)
End of Two-Phase Shunt
Three-Phase Shunt |  | Go to Type List
ID | Status1 | Status2 | Status3 | kV (ph-gr RMS) | Bus1 | Bus2 | Bus3 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
cap844 | 1 | 1 | 1 | 14.38 | 844_a | 844_b | 844_c | 0 | -100 | 0 | -100 | 0 | -100
cap848 | 1 | 1 | 1 | 14.38 | 848_a | 848_b | 848_c | 0 | -150 | 0 | -150 | 0 | -150
End of Three-Phase Shunt