## General
Excel file version | v2.0
Name | Distribution
Frequency (Hz) | 60
Power Base (MVA) | 40

## Pins
outgoing | V_abs | 633_a/Vmag | 633_b/Vmag | 633_c/Vmag | 634_a/Vmag | 634_b/Vmag | 634_c/Vmag | 611_c/Vmag | 675_a/Vmag | 675_b/Vmag | 675_c/Vmag | 632_a/Vmag | 632_b/Vmag | 632_c/Vmag
outgoing | V_ang | 633_a/Vang | 633_b/Vang | 633_c/Vang | 634_a/Vang | 634_b/Vang | 634_c/Vang | 611_c/Vang | 675_a/Vang | 675_b/Vang | 675_c/Vang | 632_a/Vang | 632_b/Vang | 632_c/Vang
outgoing | I_abs | LN_651_632/ImagFrom1 | LN_651_632/ImagFrom2 | LN_651_632/ImagFrom3 | LN_632_633/ImagFrom1 | LN_632_633/ImagFrom2 | LN_632_633/ImagFrom3
outgoing | I_ang | LN_651_632/IangFrom1 | LN_651_632/IangFrom2 | LN_651_632/IangFrom3 | LN_632_633/IangFrom1 | LN_632_633/IangFrom2 | LN_632_633/IangFrom3
outgoing | PQ_ld | LD_645/P1 | LD_645/Q1
incoming | Trans_tap | TR1_633_634/tap_1 | TR1_633_634/tap_2 | TR1_633_634/tap_3
incoming | PQ_ld | LD_645/P1 | LD_645/Q1

## Bus
Bus | Base Voltage (V) | Initial Vmag | Unit (V, pu) | Angle (deg) | Type
611_c | 2401.7771 | 2401.7771 | V | 115 | PQ
632_a | 2401.7771 | 2401.7771 | V | -2.6 | PQ
632_b | 2401.7771 | 2401.7771 | V | -121.7 | PQ
632_c | 2401.7771 | 2401.7771 | V | 117.3 | PQ
633_a | 2401.7771 | 2401.7771 | V | -2.6 | PQ
633_b | 2401.7771 | 2401.7771 | V | -121.8 | PQ
633_c | 2401.7771 | 2401.7771 | V | 117.3 | PQ
634_a | 277.1281 | 277.1281 | V | -3.4 | PQ
634_b | 277.1281 | 277.1281 | V | -122.3 | PQ
634_c | 277.1281 | 277.1281 | V | 116.8 | PQ
645_b | 2401.7771 | 2401.7771 | V | -121.9 | PQ
645_c | 2401.7771 | 2401.7771 | V | 117.2 | PQ
646_b | 2401.7771 | 2401.7771 | V | -122 | PQ
646_c | 2401.7771 | 2401.7771 | V | 117.2 | PQ
650_a | 2401.7771 | 2401.7771 | V | 0 | SLACK
650_b | 2401.7771 | 2401.7771 | V | -120 | SLACK
650_c | 2401.7771 | 2401.7771 | V | 120 | SLACK
651_a | 2401.7771 | 2401.7771 | V | 0 | PQ
651_b | 2401.7771 | 2401.7771 | V | -120 | PQ
651_c | 2401.7771 | 2401.7771 | V | 120 | PQ
652_a | 2401.7771 | 2401.7771 | V | -5.9 | PQ
671_a | 2401.7771 | 2401.7771 | V | -5.9 | PQ
671_b | 2401.7771 | 2401.7771 | V | -122 | PQ
671_c | 2401.7771 | 2401.7771 | V | 115.2 | PQ
675_a | 2401.7771 | 2401.7771 | V | -6.2 | PQ
675_b | 2401.7771 | 2401.7771 | V | -122.1 | PQ
675_c | 2401.7771 | 2401.7771 | V | 115.3 | PQ
680_a | 2401.7771 | 2401.7771 | V | -5.9 | PQ
680_b | 2401.7771 | 2401.7771 | V | -122 | PQ
680_c | 2401.7771 | 2401.7771 | V | 115.2 | PQ
684_a | 2401.7771 | 2401.7771 | V | -6 | PQ
684_c | 2401.7771 | 2401.7771 | V | 115.1 | PQ
692_a | 2401.7771 | 2401.7771 | V | -5.9 | PQ
692_b | 2401.7771 | 2401.7771 | V | -122 | PQ
692_c | 2401.7771 | 2401.7771 | V | 115.2 | PQ
Note on C1: In transmission studies, use per-unit values. In distribution studies, use V.

## Voltage Source
Type
PositiveSeqVsource
SinglePhaseVsource
ThreePhaseShortCircuitVsource
ThreePhaseSequentialVsource
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Voltage Source |  |  |  | Go to Type List
ID | Bus | Voltage (pu) | Angle (deg) | Rs (pu) | Xs (pu)
End of Positive-Sequence Voltage Source
Single-Phase Voltage Source |  |  |  | Go to Type List
ID | Bus1 | Voltage (V) | Angle (deg) | Rs (Ohm) | Xs (Ohm)
End of Single-Phase Voltage Source
Three-Phase Voltage Source with Short-Circuit Level Data |  |  |  | Go to Type List
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | SC1ph (MVA) | SC3ph (MVA)
SOURCE_A | 650_a | 650_b | 650_c | 4.16 | 0 | 200000 | 200000
End of Three-Phase Voltage Source Short-Circuit Level Data
Three-Phase Voltage Source with Sequential Data |  |  |  | Go to Type List
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | R1 (Ohm) | X1 (Ohm) | R0 (Ohm) | X0 (Ohm)
End of Three-Phase Voltage Source Sequential Data
Note on A19: Defult Assumption X1/R1 = 4 X0/R0 = 3

## Load
Type
PositiveSeqZload | ThreePhaseZIPLoad
PositiveSeqPload
PositiveSeqIload
SinglePhaseZIPLoad
TwoPhaseZIPLoad
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Constant Impedance Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Constant Impedance Load
Positive-Sequence Constant Power Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Constant Power Load
Positive-Sequence Constant Current Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Constant Current Load
Single-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | P1 (kW) | Q1 (kVAr)
LD_645 | 1 | 4.16 | 0.2 | wye | 0 | 0 | 1 | 0 | 645_b | 170 | 125
LD_646 | 1 | 4.16 | 0.2 | wye | 1 | 0 | 0 | 0 | 646_b | 230 | 132
LD_652 | 1 | 4.16 | 0.2 | wye | 1 | 0 | 0 | 0 | 652_a | 128 | 86
LD_692 | 1 | 4.16 | 0.2 | wye | 0 | 1 | 0 | 0 | 692_c | 170 | 151
LD_611 | 1 | 4.16 | 0.2 | wye | 0 | 1 | 0 | 0 | 611_c | 170 | 80
End of SinglePhase ZIP Load
Two-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | P1(kW) | Q1(kVAr) | P2 (kW) | Q2 (kVAr)
End of TwoPhase ZIP Load
Three-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | Bus3 | P1(kW) | Q1(kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
LD_634 | 1 | 0.48 | 0.2 | wye | 0 | 0 | 1 | 0 | 634_a | 634_b | 634_c | 160 | 110 | 120 | 90 | 120 | 90
LD_671 | 1 | 4.16 | 0.2 | wye | 0 | 0 | 1 | 0 | 671_a | 671_b | 671_c | 385 | 220 | 385 | 220 | 385 | 220
LD_675 | 1 | 4.16 | 0.2 | wye | 0 | 0 | 1 | 0 | 675_a | 675_b | 675_c | 485 | 190 | 68 | 60 | 290 | 212
LD_632 | 1 | 4.16 | 0.2 | wye | 0 | 0 | 1 | 0 | 632_a | 632_b | 632_c | 17 | 10 | 66 | 38 | 117 | 68
End of ThreePhase ZIP Load
Note on B24: 0: out-of-service 1: in-service
Note on C24: phase-to-phase RMS voltage
Note on E24: wye: for Yg delta: for D
Note on I24: 0: Power is specified at the given nominal voltage 1: Power is specified for the voltage value in page Bus
Note on B33: 0: out-of-service 1: in-service
Note on C33: phase-to-phase RMS voltage
Note on E33: wye: for Yg delta: for D
Note on I33: 0: Power is specified at the given nominal voltage 1: Power is specified for the voltage value in page Bus
Note on B37: 0: out-of-service 1: in-service
Note on C37: phase-to-phase RMS voltage
Note on E37: wye: for Yg delta: for D
Note on I37: 0: Power is specified at the given nominal voltage 1: Power is specified for the voltage value in page Bus

## Line
Type
PositiveSeqLine
SinglePhaseLine
TwoPhaseLine
ThreePhaseLineFullData
ThreePhaseLineSequentialData
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Line |  | Go to Type List
ID | Status | From bus | To bus | R (pu) | X (pu) | B (pu)
End of Positive-Sequence Line
Single-Phase Line |  | Go to Type List
ID | Status | Length | From1 | To1 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | b11 (uS/length_unit)
LN_684_611 | 1 | 0.056818 | 684_c | 611_c | 1.3292 | 1.3475 | 4.5193
LN_684_652 | 1 | 0.15152 | 684_a | 652_a | 1.3425 | 0.5124 | 88.9699
End of Single-Phase Line
Two-Phase Line |  | Go to Type List
ID | Status | Length | From1 | From2 | To1 | To2 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit)
LN_645_646 | 1 | 0.056818 | 645_b | 645_c | 646_b | 646_c | 1.3238 | 1.3569 | 0.2066 | 0.4591 | 1.3294 | 1.3471 | 4.6658 | -0.8999 | 4.7097
LN_632_645 | 1 | 0.094697 | 632_b | 632_c | 645_b | 645_c | 1.3238 | 1.3569 | 0.2066 | 0.4591 | 1.3294 | 1.3471 | 4.6658 | -0.8999 | 4.7097
LN_671_684 | 1 | 0.056818 | 671_a | 671_c | 684_a | 684_c | 1.3238 | 1.3569 | 0.2066 | 0.4591 | 1.3294 | 1.3471 | 4.6658 | -0.8999 | 4.7097
End of Two-Phase Line
Three-Phase Line with Full Data |  | Go to Type List
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | r31 (Ohm/length_unit) | x31 (Ohm/length_unit) | r32 (Ohm/length_unit) | x32 (Ohm/length_unit) | r33 (Ohm/length_unit) | x33 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit) | b31 (uS/length_unit) | b32 (uS/length_unit) | b33 (uS/length_unit)
LN_632_671 | 1 | 0.37879 | 632_a | 632_b | 632_c | 671_a | 671_b | 671_c | 0.3465 | 1.0179 | 0.156 | 0.5017 | 0.3375 | 1.0478 | 0.158 | 0.4236 | 0.1535 | 0.3849 | 0.3414 | 1.0348 | 6.2998 | -1.9958 | 5.9597 | -1.2595 | -0.7417 | 5.6386
LN_671_680 | 1 | 0.18939 | 671_a | 671_b | 671_c | 680_a | 680_b | 680_c | 0.3465 | 1.0179 | 0.156 | 0.5017 | 0.3375 | 1.0478 | 0.158 | 0.4236 | 0.1535 | 0.3849 | 0.3414 | 1.0348 | 6.2998 | -1.9958 | 5.9597 | -1.2595 | -0.7417 | 5.6386
LN_651_632 | 1 | 0.37879 | 651_a | 651_b | 651_c | 632_a | 632_b | 632_c | 0.3465 | 1.0179 | 0.156 | 0.5017 | 0.3375 | 1.0478 | 0.158 | 0.4236 | 0.1535 | 0.3849 | 0.3414 | 1.0348 | 6.2998 | -1.9958 | 5.9597 | -1.2595 | -0.7417 | 5.6386
LN_632_633 | 1 | 0.094697 | 632_a | 632_b | 632_c | 633_a | 633_b | 633_c | 0.7526 | 1.1814 | 0.158 | 0.4236 | 0.7475 | 1.1983 | 0.156 | 0.5017 | 0.1535 | 0.3849 | 0.7436 | 1.2112 | 5.699 | -1.0817 | 5.1795 | -1.6905 | -0.6588 | 5.4246
LN_692_675 | 1 | 0.094697 | 692_a | 692_b | 692_c | 675_a | 675_b | 675_c | 0.7982 | 0.4463 | 0.3192 | 0.0328 | 0.7891 | 0.4041 | 0.2849 | -0.0143 | 0.3192 | 0.0328 | 0.7982 | 0.4463 | 96.8867 | 0 | 96.8867 | 0 | 0 | 96.8867
End of Three-Phase Line with Full Data
Three-Phase Line with Sequential Data |  | Go to Type List
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | R0 (Ohm/length_unit) | X0 (Ohm/length_unit) | R1 (Ohm/length_unit) | X1 (Ohm/length_unit) | B0 (uS/length_unit) | B1 (uS/length_unit)
End of Three-Phase Line with Sequential Data

## Transformer
Type
PositiveSeq2wXF
PositiveSeq3wXF
Multiphase2wXF
Multiphase2wXFMutual
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence 2W-Transformer |  |  | Go to Type List
ID | Status | From bus | To bus | R (pu) | Xl (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Phase Shift (deg)
End of Positive-Sequence 2W-Transformer
Positive-Sequence 3W-Transformer |  |  | Go to Type List
ID | Status | Bus1 | Bus2 | Bus3 | R_12 (pu) | Xl_12 (pu) | R_23 (pu) | Xl_23 (pu) | R_31 (pu) | Xl_31 (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Ratio W3 (pu) | Phase Shift W1 (deg) | Phase Shift W2 (deg) | Phase Shift W3 (deg)
End of Positive-Sequence 3W-Transformer
Multiphase 2W-Transformer |  |  | Go to Type List
ID | Status | Number of phases | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | X (pu) | RW1 (pu) | RW2 (pu)
TR1_633_634 | 1 | 3 | 633_a | 633_b | 633_c | 4.16 | 500 | wye | 634_a | 634_b | 634_c | 0.48 | 500 | wye | 0 | 0 | 0 | -16 | 16 | 10 | 10 | 0.02 | 0.0055 | 0.0055
TR1_650_651 | 1 | 3 | 650_a | 650_b | 650_c | 4.16 | 5000 | wye | 651_a | 651_b | 651_c | 4.16 | 5000 | wye | 0 | 0 | 0 | -16 | 16 | 10 | 10 | 0.0001 | 4.98e-06 | 4.98e-06
End of Multiphase 2W-Transformer
Multiphase 2W-Transformer with Mutual Impedance |  |  | Go to Type List
ID | Status | Number of phases | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | Z0 leakage (pu) | Z1 leakage (pu) | X0/R0 | X1/R1 | No Load Loss (kW)
End of Multiphase 2W-Transformer with Mutual Impedance
Note on G20: phase-to-phase RMS voltage
Note on I20: wye: for Yg delta: for D
Note on M20: phase-to-phase RMS voltage
Note on N20: not applicable, to be removed in future versions
Note on O20: wye: for Yg delta: for D
Note on G26: phase-to-phase RMS voltage
Note on I26: wye: for Yg delta: for D
Note on M26: phase-to-phase RMS voltage
Note on N26: not applicable, to be removed in future versions
Note on O26: wye: for Yg delta: for D
Note on AA26: This value is not used.

## Shunt
Type
PositiveSeqShunt
SinglePhaseShunt
TwoPhaseShunt
ThreePhaseShunt
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Shunt |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Shunt
Single-Phase Shunt |  | Go to Type List
ID | Status | kV (ph-gr RMS) | Bus1 | P1 (kW) | Q1 (kVAr)
cap611 | 1 | 2.4018 | 611_c | 0 | -100
End of Single-Phase Shunt
Two-Phase Shunt |  | Go to Type List
ID | Status1 | Status2 | kV (ph-gr RMS) | Bus1 | Bus2 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr)
End of Two-Phase Shunt
Three-Phase Shunt |  | Go to Type List
ID | Status1 | Status2 | Status3 | kV (ph-gr RMS) | Bus1 | Bus2 | Bus3 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
cap675 | 1 | 1 | 1 | 2.4018 | 675_a | 675_b | 675_c | 0 | -200 | 0 | -200 | 0 | -200
End of Three-Phase Shunt

## Switch
From Bus | To Bus | ID | Status
671_a | 692_a | SW_671_692_a | 1
671_b | 692_b | SW_671_692_b | 1
671_c | 692_c | SW_671_692_c | 1
Note on D1: 0: open 1: closed