## General
Excel file version | v2.0
Name | Distribution
Frequency (Hz) | 67
Power Base (MVA) | 117

## Pins
outgoing | V_abs | 611_c/Vmag | 632_a/Vmag | 632_b/Vmag | 632_c/Vmag | 634_a/Vmag | 634_b/Vmag | 634_c/Vmag | 645_b/Vmag | 645_c/Vmag | 646_b/Vmag | 646_c/Vmag | 652_a/Vmag | 671_a/Vmag | 671_b/Vmag | 671_c/Vmag | 675_a/Vmag | 675_b/Vmag | 675_c/Vmag | 680_a/Vmag | 680_b/Vmag | 680_c/Vmag | 684_a/Vmag | 684_c/Vmag | 692_a/Vmag | 692_b/Vmag | 692_c/Vmag
outgoing | V_ang | 611_c/Vang | 632_a/Vang | 632_b/Vang | 632_c/Vang | 634_a/Vang | 634_b/Vang | 634_c/Vang | 645_b/Vang | 645_c/Vang | 646_b/Vang | 646_c/Vang | 652_a/Vang | 671_a/Vang | 671_b/Vang | 671_c/Vang | 675_a/Vang | 675_b/Vang | 675_c/Vang | 680_a/Vang | 680_b/Vang | 680_c/Vang | 684_a/Vang | 684_c/Vang | 692_a/Vang | 692_b/Vang | 692_c/Vang
outgoing | I_abs | LN_632_633/ImagFrom1 | LN_632_633/ImagFrom2 | LN_632_633/ImagFrom3 | LN_632_645/ImagFrom1 | LN_632_645/ImagFrom2 | LN_632_671/ImagFrom1 | LN_632_671/ImagFrom2 | LN_632_671/ImagFrom3 | LN_645_646/ImagFrom1 | LN_645_646/ImagFrom2 | LN_671_680/ImagFrom1 | LN_671_680/ImagFrom2 | LN_671_680/ImagFrom3 | LN_671_684/ImagFrom1 | LN_671_684/ImagFrom2 | LN_684_611/ImagFrom1 | LN_684_652/ImagFrom1 | LN_692_675/ImagFrom1 | LN_692_675/ImagFrom2 | LN_692_675/ImagFrom3
outgoing | I_ang | LN_632_633/IangFrom1 | LN_632_633/IangFrom2 | LN_632_633/IangFrom3 | LN_632_645/IangFrom1 | LN_632_645/IangFrom2 | LN_632_671/IangFrom1 | LN_632_671/IangFrom2 | LN_632_671/IangFrom3 | LN_645_646/IangFrom1 | LN_645_646/IangFrom2 | LN_671_680/IangFrom1 | LN_671_680/IangFrom2 | LN_671_680/IangFrom3 | LN_671_684/IangFrom1 | LN_671_684/IangFrom2 | LN_684_611/IangFrom1 | LN_684_652/IangFrom1 | LN_692_675/IangFrom1 | LN_692_675/IangFrom2 | LN_692_675/IangFrom3
outgoing | PQ_ld | LD_611/P1 | LD_611/Q1 | LD_634/P1 | LD_634/Q1 | LD_634/P2 | LD_634/Q2 | LD_634/P3 | LD_634/Q3 | LD_645/P1 | LD_645/Q1 | LD_646/P1 | LD_646/Q1 | LD_646/P2 | LD_646/Q2 | LD_652/P1 | LD_652/Q1 | LD_671/P1 | LD_671/Q1 | LD_671/P2 | LD_671/Q2 | LD_671/P3 | LD_671/Q3 | LD_675/P1 | LD_675/Q1 | LD_675/P2 | LD_675/Q2 | LD_675/P3 | LD_675/Q3 | LD_692/P1 | LD_692/Q1 | LD_692/P2 | LD_692/Q2
incoming | Trans_tap | TR1_633_634/tap_1 | TR1_633_634/tap_2 | TR1_633_634/tap_3
incoming | PQ_ld | LD_611/P1 | LD_611/Q1 | LD_634/P1 | LD_634/Q1 | LD_634/P2 | LD_634/Q2 | LD_634/P3 | LD_634/Q3 | LD_645/P1 | LD_645/Q1 | LD_646/P1 | LD_646/Q1 | LD_646/P2 | LD_646/Q2 | LD_652/P1 | LD_652/Q1 | LD_671/P1 | LD_671/Q1 | LD_671/P2 | LD_671/Q2 | LD_671/P3 | LD_671/Q3 | LD_675/P1 | LD_675/Q1 | LD_675/P2 | LD_675/Q2 | LD_675/P3 | LD_675/Q3 | LD_692/P1 | LD_692/Q1 | LD_692/P2 | LD_692/Q2

## Bus
Bus | Base Voltage (V) | Initial Vmag | Unit | Angle | Type
611_c | 2401.777 | 2401.777 | V | 120 | PQ
632_a | 2401.777 | 2401.777 | V | 0 | PQ
632_b | 2401.777 | 2401.777 | V | -120 | PQ
632_c | 2401.777 | 2401.777 | V | 120 | PQ
633_a | 2401.777 | 2401.777 | V | 0 | PQ
633_b | 2401.777 | 2401.777 | V | -120 | PQ
633_c | 2401.777 | 2401.777 | V | 120 | PQ
634_a | 2401.777 | 2401.777 | V | 0 | PQ
634_b | 2401.777 | 2401.777 | V | -120 | PQ
634_c | 2401.777 | 2401.777 | V | 120 | PQ
645_b | 2401.777 | 2401.777 | V | -120 | PQ
645_c | 2401.777 | 2401.777 | V | 120 | PQ
646_b | 2401.777 | 2401.777 | V | -120 | PQ
646_c | 2401.777 | 2401.777 | V | 120 | PQ
650_a | 2401.777 | 2401.777 | V | 0 | Slack
650_b | 2401.777 | 2401.777 | V | -120 | Slack
650_c | 2401.777 | 2401.777 | V | 120 | Slack
651_a | 2401.777 | 2401.777 | V | 0 | PQ
651_b | 2401.777 | 2401.777 | V | -120 | PQ
651_c | 2401.777 | 2401.777 | V | 120 | PQ
652_a | 2401.777 | 2401.777 | V | 0 | PQ
671_a | 2401.777 | 2401.777 | V | 0 | PQ
671_b | 2401.777 | 2401.777 | V | -120 | PQ
671_c | 2401.777 | 2401.777 | V | 120 | PQ
675_a | 2401.777 | 2401.777 | V | 0 | PQ
675_b | 2401.777 | 2401.777 | V | -120 | PQ
675_c | 2401.777 | 2401.777 | V | 120 | PQ
680_a | 2401.777 | 2401.777 | V | 0 | PQ
680_b | 2401.777 | 2401.777 | V | -120 | PQ
680_c | 2401.777 | 2401.777 | V | 120 | PQ
684_a | 2401.777 | 2401.777 | V | 0 | PQ
684_c | 2401.777 | 2401.777 | V | 120 | PQ
692_a | 2401.777 | 2401.777 | V | 0 | PQ
692_b | 2401.777 | 2401.777 | V | -120 | PQ
692_c | 2401.777 | 2401.777 | V | 120 | PQ

## Voltage Source
Type
PositiveSeqVsource
SinglePhaseVsource
ThreePhaseShortCircuitVsource
ThreePhaseSequentialVsource
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Voltage Source |  |  |  | Go to Type List
ID | Bus | Voltage (pu) | Angle (deg) | Rs (pu) | Xs (pu)
End of Positive-Sequence Voltage Source
Single-Phase Voltage Source |  |  |  | Go to Type List
ID | Bus1 | Voltage (V) | Angle (deg) | Rs (Ohm) | Xs (Ohm)
End of Single-Phase Voltage Source
Three-Phase Voltage Source with Short-Circuit Level Data |  |  |  | Go to Type List
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | SC1ph (MVA) | SC3ph (MVA)
SUB650WYE | 650_a | 650_b | 650_c | 4.16 | 0 | 200000 | 200000
End of Three-Phase Voltage Source with Short-Circuit Level Data
Three-Phase Voltage Source with Sequential Data |  |  |  | Go to Type List
ID | Bus1 | Bus2 | Bus3 | kV (ph-ph RMS) | Angle_a (deg) | R1 (Ohm) | X1 (Ohm) | R0 (Ohm) | X0 (Ohm)
End of Three-Phase Voltage Source with Sequential Data

## Load
Type
PositiveSeqZload | ThreePhaseZIPLoad
PositiveSeqPload
PositiveSeqIload
SinglePhaseZIPLoad
TwoPhaseZIPLoad
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Constant Impedance Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Constant Impedance Load
Positive-Sequence Constant Power Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Constant Power Load
Positive-Sequence Constant Current Load |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Constant Current Load
Single-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | P1 (kW) | Q1 (kVAr)
LD_645 | 1 | 4.16 | 0.2 | wye | 0 | 0 | 1 | 0 | 645_b | 170 | 125
LD_652 | 1 | 4.16 | 0.2 | wye | 1 | 0 | 0 | 0 | 652_a | 128 | 86
LD_611 | 1 | 4.16 | 0.2 | wye | 0 | 1 | 0 | 0 | 611_c | 170 | 80
End of SinglePhase ZIP Load
Two-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | P1(kW) | Q1(kVAr) | P2 (kW) | Q2 (kVAr)
LD_692 | 1 | 4.16 | 0.2 | wye | 0 | 1 | 0 | 0 | 692_a | 692_c | 0 | 0 | 170 | 151
LD_646 | 1 | 4.16 | 0.2 | wye | 1 | 0 | 0 | 0 | 646_b | 646_c | 230 | 132 | 0 | 0
End of TwoPhase ZIP Load
Three-Phase ZIP Load |  | Go to Type List
ID | Status | V (kV) | Bandwidth (pu) | Conn. type | K_z | K_i | K_p | Use initial voltage? | Bus1 | Bus2 | Bus3 | P1(kW) | Q1(kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
LD_675 | 1 | 4.16 | 0.2 | wye | 0 | 0 | 1 | 0 | 675_a | 675_b | 675_c | 485 | 190 | 68 | 60 | 290 | 212
LD_634 | 1 | 0.48 | 0.2 | wye | 0 | 0 | 1 | 0 | 634_a | 634_b | 634_c | 160 | 110 | 120 | 90 | 120 | 90
LD_671 | 1 | 4.16 | 0.2 | wye | 0 | 0 | 1 | 0 | 671_a | 671_b | 671_c | 385 | 220 | 385 | 220 | 385 | 220
End of Three-Phase ZIP Load

## Line
Type
PositiveSeqLine
SinglePhaseLine
TwoPhaseLine
ThreePhaseLineFullData
ThreePhaseLineSequentialData
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Line |  | Go to Type List
ID | Status | From bus | To bus | R (pu) | X (pu) | B (pu)
End of Positive-Sequence Line
Single-Phase Line |  | Go to Type List
ID | Status | Length | From1 | To1 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | b11 (uS/length_unit)
LN_684_652 | 1 | 0.15152 | 684_a | 652_a | 0.51834 | 0.19784 | 34.3597
LN_684_611 | 1 | 0.056818 | 684_c | 611_c | 0.51112 | 0.5239 | 1.8015
End of Single-Phase Line
Two-Phase Line |  | Go to Type List
ID | Status | Length | From1 | From2 | To1 | To2 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit)
LN_671_684 | 1 | 0.056818 | 671_a | 671_c | 684_a | 684_c | 0 | 0 | 0 | 0 | 0.51112 | 0.5239 | 0 | 0 | 1.8015
LN_632_645 | 1 | 0.094697 | 632_b | 632_c | 645_b | 645_c | 0.51328 | 0.52012 | 0.079769 | 0.17726 | 0.51112 | 0.5239 | 1.8184 | -0.34745 | 1.8015
LN_645_646 | 1 | 0.056818 | 645_b | 645_c | 646_b | 646_c | 0.51328 | 0.52012 | 0.079769 | 0.17726 | 0.51112 | 0.5239 | 1.8184 | -0.34745 | 1.8015
End of Two-Phase Line
Three-Phase Line with Full Data |  | Go to Type List
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | r11 (Ohm/length_unit) | x11 (Ohm/length_unit) | r21 (Ohm/length_unit) | x21 (Ohm/length_unit) | r22 (Ohm/length_unit) | x22 (Ohm/length_unit) | r31 (Ohm/length_unit) | x31 (Ohm/length_unit) | r32 (Ohm/length_unit) | x32 (Ohm/length_unit) | r33 (Ohm/length_unit) | x33 (Ohm/length_unit) | b11 (uS/length_unit) | b21 (uS/length_unit) | b22 (uS/length_unit) | b31 (uS/length_unit) | b32 (uS/length_unit) | b33 (uS/length_unit)
LN_651_632 | 1 | 0.37879 | 651_a | 651_b | 651_c | 632_a | 632_b | 632_c | 0.13378 | 0.39301 | 0.060155 | 0.16861 | 0.13031 | 0.40456 | 0.060155 | 0.16861 | 0.060155 | 0.16861 | 0.13182 | 0.39954 | 2.4324 | -0.5144 | 2.3011 | -0.5144 | -0.5144 | 2.1771
LN_671_680 | 1 | 0.18939 | 671_a | 671_b | 671_c | 680_a | 680_b | 680_c | 0.13378 | 0.39301 | 0.060155 | 0.16861 | 0.13031 | 0.40456 | 0.060155 | 0.16861 | 0.060155 | 0.16861 | 0.13182 | 0.39954 | 2.4324 | -0.5144 | 2.3011 | -0.5144 | -0.5144 | 2.1771
LN_632_633 | 1 | 0.094697 | 632_a | 632_b | 632_c | 633_a | 633_b | 633_c | 0.13378 | 0.39301 | 0.060155 | 0.16861 | 0.13031 | 0.40456 | 0.060155 | 0.16861 | 0.060155 | 0.16861 | 0.13182 | 0.39954 | 2.4324 | -0.5144 | 2.3011 | -0.5144 | -0.5144 | 2.1771
LN_692_675 | 1 | 0.094697 | 692_a | 692_b | 692_c | 675_a | 675_b | 675_c | 0.30819 | 0.17232 | 0.11884 | 0.0066021 | 0.30467 | 0.15602 | 0.11884 | 0.0066021 | 0.11884 | 0.0066021 | 0.30819 | 0.17232 | 37.4093 | 0 | 37.4093 | 0 | 0 | 37.4093
LN_632_671 | 1 | 0.37879 | 632_a | 632_b | 632_c | 671_a | 671_b | 671_c | 0.13378 | 0.39301 | 0.060155 | 0.16861 | 0.13031 | 0.40456 | 0.060155 | 0.16861 | 0.060155 | 0.16861 | 0.13182 | 0.39954 | 2.4324 | -0.5144 | 2.3011 | -0.5144 | -0.5144 | 2.1771
End of Three-Phase Line with Full Data
Three-Phase Line with Sequential Data |  | Go to Type List
ID | Status | Length | From1 | From2 | From3 | To1 | To2 | To3 | R0 (Ohm/length_unit) | X0 (Ohm/length_unit) | R1 (Ohm/length_unit) | X1 (Ohm/length_unit) | B0 (uS/length_unit) | B1 (uS/length_unit)
End of Three-Phase Line with Sequential Data

## Transformer
Type
PositiveSeq2wXF
PositiveSeq3wXF
Multiphase2wXF
Multiphase2wXFMutual
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence 2W-Transformer |  |  | Go to Type List
ID | Status | From bus | To bus | R (pu) | Xl (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Phase Shift (deg)
End of Positive-Sequence 2W-Transformer
Positive-Sequence 3W-Transformer |  |  | Go to Type List
ID | Status | Bus1 | Bus2 | Bus3 | R_12 (pu) | Xl_12 (pu) | R_23 (pu) | Xl_23 (pu) | R_31 (pu) | Xl_31 (pu) | Gmag (pu) | Bmag (pu) | Ratio W1 (pu) | Ratio W2 (pu) | Ratio W3 (pu) | Phase Shift W1 (deg) | Phase Shift W2 (deg) | Phase Shift W3 (deg)
End of Positive-Sequence 3W-Transformer
Multiphase 2W-Transformer |  |  | Go to Type List
ID | Status | Number of phases | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | X (pu) | RW1 (pu) | RW2 (pu)
TR1_633_634 | 1 | 3 | 633_a | 633_b | 633_c | 4.16 | 500.001 | wye | 634_a | 634_b | 634_c | 0.48 | 500.001 | wye | 0 | 0 | 0 | -16 | 16 | 10 | 10 | 0.02 | 0.0055001 | 0.0055001
End of Multiphase 2W-Transformer
Multiphase 2W-Transformer with Mutual Impedance |  |  | Go to Type List
ID | Status | Number of phases | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Bus1 | Bus2 | Bus3 | V (kV) | S_base (kVA) | Conn. type | Tap 1 | Tap 2 | Tap 3 | Lowest Tap | Highest Tap | Min Range (%) | Max Range (%) | Z0 leakage (pu) | Z1 leakage (pu) | X0/R0 | X1/R1 | No Load Loss (kW)
End of Multiphase 2W-Transformer with Mutual Impedance

## Shunt
Type
PositiveSeqShunt
SinglePhaseShunt
TwoPhaseShunt
ThreePhaseShunt
Important notes:
Default order of blocks and columns after row 11 must not change
One empty row between End of each block and the next block is mandatory; otherwise, empty rows are NOT allowed
Positive-Sequence Shunt |  | Go to Type List
ID | Status | Bus | P (MW) | Q (MVAr)
End of Positive-Sequence Shunt
Single-Phase Shunt |  | Go to Type List
ID | Status | kV (ph-gr RMS) | Bus1 | P1 (kW) | Q1 (kVAr)
cap611 | 1 | 2.4018 | 611_c | 0 | -100
End of Single-Phase Shunt
Two-Phase Shunt |  | Go to Type List
ID | Status1 | Status2 | kV (ph-gr RMS) | Bus1 | Bus2 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr)
End of Two-Phase Shunt
Three-Phase Shunt |  | Go to Type List
ID | Status1 | Status2 | Status3 | kV (ph-gr RMS) | Bus1 | Bus2 | Bus3 | P1 (kW) | Q1 (kVAr) | P2 (kW) | Q2 (kVAr) | P3 (kW) | Q3 (kVAr)
cap675 | 1 | 1 | 1 | 2.4018 | 675_a | 675_b | 675_c | 0 | -200 | 0 | -200 | 0 | -200
End of Three-Phase Shunt

## Switch
From Bus | To Bus | ID | Status
650_a | 651_a | SW_650_651_a | 1
650_b | 651_b | SW_650_651_b | 1
650_c | 651_c | SW_650_651_c | 1
671_a | 692_a | SW_671_692_a | 1
671_b | 692_b | SW_671_692_b | 1
671_c | 692_c | SW_671_692_c | 1